## Spot inspection
Spot inspection
A: "light plan" B: "standard plan" C: "premium light plan" D: "premium plan"
| Equipment classification | Inspection items |  | Inspection details | A | B | C | D
| solar cell module (Around the panel)・Panel installation frame | Visually | Dirty/damaged panel surface | Check for broken glass, dirt, bird droppings, yellow sand, etc. | ● | ● | ● | ●
|  |  | Damage/deformation of panel frame | Check for damage or deformation of panel frame | ● | ● | ● | ●
|  |  | Damage/disconnection of panel cable | Check for scratches and cracks on the cable | ● | ● | ● | ●
|  |  | Weeds that cause shadows | Checking for weeds that cause shadows | ● | ● | ● | ●
|  |  | Small animals that interfere with power generation | Check for small animals that interfere with power generation (remove those that can be removed) | ● | ● | ● | ●
|  |  | Damaged/loose connector | Check for damaged/loose connectors | ● | ● | ● | ●
|  |  | Corrosion/rust of the frame | Check for corrosion/rust | ● | ● | ● | ●
|  |  | Looseness/rust of frame bolts | Check for looseness and rust | ● | ● | ● | ●
|  |  | Deformation of the pedestal | Checking deformation and horizontal/vertical levels | ● | ● | ● | ●
|  | measurement | IR measurement | Judgment by thermography | - | - | ● | ●
|  |  | Defect location identification | Defect identification using measuring instruments | - | - | ● | ●
|  |  | Leakage current check | Defect identification using measuring instruments | - | ● | ● | ●
| AC current collection box | Visually | Check appearance of outer box | Mainly check for rust | ● | ● | ● | ●
|  |  | Fixing the outer box | Check for looseness of fixing bolts | ● | ● | ● | ●
|  |  | Waterproofing | Check caulking and putty treatment | ● | ● | ● | ●
|  |  | Loose screws on the terminal block | Check for loose screws | ● | ● | ● | ●
|  |  | Check the appearance of the terminal part | Confirmation of burnout of terminal part | ● | ● | ● | ●
|  | measurement | Voltage (AC current collection box) | voltage measurement | ● | ● | ● | ●
|  |  | Current (AC current collection box) | current measurement | ● | ● | ● | ●
|  |  | Leakage current check | 0 phase measurement with clamp | - | ● | ● | ●
| cable | Visually | Cable damage/disconnection (between module connection boxes) | Check for scratches and cracks on the cable | - | ● | ● | ●
|  |  | Cable damage/disconnection (junction box, power controller, AC current collector box) | Check for scratches and cracks on the cable | - | ● | ● | ●
|  |  | Check cable protection | Fixing and deterioration confirmation of PFD, VE pipe, metal pipe, rack, etc. | - | ● | ● | ●
| power conditioner | Visually | Corrosion/damage to the outer box | Check for corrosion/damage | ● | ● | ● | ●
|  |  | Checking operation, errors, and supine | Check with display device, display panel, and setting values | ● | ● | ● | ●
|  |  | Check power generation amount | Check current power generation amount | ● | ● | ● | ●
|  |  | Cleaning and checking the filter | Check the filter part visually and by palpation | ● | ● | ● | ●
|  |  | Cleaning and inspection of fans | Check air volume and abnormal noise | ● | ● | ● | ●
|  |  | Check for loose terminals and burnout | Check for looseness and burnout of terminals | ● | ● | ● | ●
|  |  | Check for abnormal noises, odors, and vibrations | Check for abnormal noises, odors, and vibrations during operation. | ● | ● | ● | ●
|  |  | Check for condensation and water leakage | Check for internal condensation and water leakage | ● | ● | ● | ●
|  |  | Check for rust | Check for rust during internal processing | ● | ● | ● | ●
|  |  | Checking the water stop material | Check the water stop status around the entry area and box | ● | ● | ● | ●
|  |  | Check fuses and circuit breakers | Check for dust, deformation, etc. | ● | ● | ● | ●
|  |  | Checking SMPS | Checking the status of the LED lamp | ● | ● | ● | ●
|  |  | Checking SPD (surge protection device) | Replace if SPD turns red. | ● | ● | ● | ●
|  |  | Check the appearance of the terminal part | Confirmation of burnout of terminal part | - | ● | ● | ●
|  |  | Check the terminal tightening torque | Check that it is tightened to the specified torque value | - | ● | ● | ●
|  |  | Check the connector of the circuit breaker and grounding part | Check for looseness of bolts and nuts tightened during construction | - | ● | ● | ●
|  |  | Checking the islanding detection function | Confirmation of protection function in case of ground fault | - | ● | ● | ●
|  | measurement | Checking insulation resistance | Insulation resistance measurement | - | ● | ● | ●
|  |  | Leakage current check | 0 phase measurement with clamp | - | ● | ● | ●
|  |  | Measuring voltage and current values | Check that each power conditioner outputs appropriate voltage and current values. | - | ● | ● | ●
|  |  | Power measurement per string | IV curve measurement | - | ● | ● | ●
|  |  | Electricity meter operation | that the meter is working properly | ● | ● | ● | ●
| others | Visually | Lost/Theft | Have equipment that meets specifications | ● | ● | ● | ●
|  |  | damaged fence | No damage | ● | ● | ● | ●
|  |  | Checking the weed situation | Check for shadow effects caused by weeds, entanglement on equipment, etc. | ● | ● | ● | ●
|  |  | Illegal dumping confirmed | Check for illegally dumped garbage | ● | ● | ● | ●
|  | measurement | See how sunlight is structured | Check the string and connection details | - | - | ● | ●
| panel cleaning | cleaning | Panel cleaning | Cleans stubborn dirt that won't come off in the rain | - | - | - | ●